5. Sample Summary File

| System | Availability | Condition | Observations |
| --- | --- | --- | --- |
| Fire Hydrant System | Yes | Partially Functional | No internal hydrants; pressure test not done |
| Sprinkler System | No | Not Installed | Required for warehouse as per storage category |
| Fire Alarm System | Yes | Obsolete | Non-addressable, no smoke detectors in key areas |
| Portable Extinguishers | Yes | Poorly Distributed | Missing in server room and electrical panel area |
| Fire Pumps & Water Storage | Yes | Inadequate | Tank undersized; diesel pump untested |
| Emergency Exits & Signage | Yes | Non-Compliant | Exit signs missing; doors not fire-rated |
| Fire Doors / Compartmentation | Partial | Inadequate | Openings in fire walls not sealed |
| Detection in Storage Racks | No | - | No in-rack sprinklers or beam detection |
| Fire NOC & AMC Records | No | Incomplete | Fire NOC expired; no AMC for pumps or alarms |